Evaluation ID: DR-draft Effective Date:

Re-evaluation Date:

Product Name: Series 0000 Vinyl Sliding Glass Doors, Fin Installation, Impact Resistant

Manufacturer: Manufacturer, Inc.

1234 Street Name

City, State Zip

(123) 456-7890

General Description:

|  |  |  |  |
| --- | --- | --- | --- |
| System | Description | Label Rating | Design Pressure Rating |
| 1 | Series 0000 Vinyl Sliding Glass Doors; OX | R-PG50 72 x 80-SD  Missile Level D | +50 / -50 psf |

Product Dimensions:

|  |  |  |  |
| --- | --- | --- | --- |
| System | Overall Size | Operable Panel Size | Fixed Panel Glass Daylight Opening Size |
| 1 | 71-1/2" x 79-1/2" | 36-13/16" x 72-3/16" | 32-3/16" x 76-3/8" |

Product Identification (Certification Agency Label on Door):

|  |  |  |
| --- | --- | --- |
| System |  | |
| 1 | Certification Agency | WDMA |
| Manufacturer’s Name or Code Name | Manufacturer, Inc |
| Product Name | Series 0000 Vinyl SGD |
| Test Standards | AAMA/WDMA/CSA 101/I.S.2/A440-08;  ASTM E 1886-09, ASTM E 1996-09;  Missile Level D |

Impact Resistance:

|  |  |  |
| --- | --- | --- |
| System | Impact Resistant | Requirement |
| 1 | Yes | These products satisfy TDI’s criteria for protection from windborne debris in the Inland I and Seaward zone. Install the assemblies at a height on the structure that does not exceed the design pressure rating for the assemblies. |

**Installation:**

Use minimum Spruce-Pine-Fir dimension lumber. Secure the assembly to the wall framing using the nailing fin with minimum No. 8 Philips pan head screws. Locate the fasteners approximately 2" from each corner and approximately 4" on center along the perimeter of the assembly. Use fasteners long enough to penetrate a minimum of 1-1/2" into the wall framing.

Note: Keep the manufacturer’s installation instructions available on the job site during installation. Use corrosion resistant fasteners as specified in the IRC, IBC, and the Texas Revisions.